## Tabelle1
Application: Stand alone system for garden house
Location: Nürnberg |  |  | La Latitude: 49,46 N
A: LOADS / lASTEN
A1 | Inverter efficiency [%] | 93
A2 | Battery Bus voltage [V] | 24
A3 | Inverter ac voltage [Vac] | 230
Verbraucher / Gerät | A4 | A5 | A6 | A7 | A8
| [W] |  | [W] | [h] | [Wh]
LED Beleuchtung (10) | 800 | 0.93 | 860.2151 | 4 | 3440.8602
Kühlschrank | 100 | 0.93 | 107.5269 | 8 | 860.2151
Einzel Induktions Kochfeld | 1000 | 0.93 | 1075.2688 | 2 | 2150.5376
A9 (Total energy demand per day) [Wh] | 6451.6129
A10 (Total amp-hour demand per day) [Ah] | 268.8172
A11 (Maximum AC power requirement) [W] | 1900
A12 (Maximum DCpower requirement) [W] | 2043.0108
B: Battery sizing / Dimensionierung der Batterie |  | Design Temp. 25°C / 77 F
B1 - Days of storage desired/required (Tage) | 3
B2 - Allowable depth-of-discharge limit (decimal) | 0.5
B3 - Required battery capacity [Ah] | 1612.9032
B4 - Amp-Hour capacity of selected battery [Ah] | 255
B5 - Number of batteries in parallel | 6.3251
B6 - Number of batteries in series | 2
B7 - Total Number of Batteries | 12.6502
B8 - Total battery amp-hour capacity [Ah] | 1612.9032
B9 - Total battery kilowatt-hour capacity [kWh] | 38.7097
B10 - Average daily depth of discharge | 0.125
C. PV Array Sizing /Dimensionierung von PV-Anlagen
LOCATION: Am Hirschfeld 6 90451 Nürnberg
C1 - Total energy demand per day [Wh] | 6451.6129
C2 - Battery round trip efficiency (0,70 - 0,85) | 0.93
C3 - Required array output per day [Wh] | 6937.2182
C4 - Selected PV module max power voltage at STC [V] | 38.316
C5 - Selected PV module guaranteed power output at STC [W] | 369
C6 - Peek sum hours at design tilt for design month | 5
C7 - Energy output per module per day [Wh] | 1845
C8 - Module energy output at operating temperature | 1660.5 | DF - HOT | DF - moderate
|  | 0.8 | 0.9
C9 - Number of modules required to meet energy requirements | 4.1778
C10 - Number of modules required per string | 0.62637
C11 - Number of strings in parallel | 6.6698
C12 - Number of modules to be purchased | 4.1778
C13 - Nominal rated PV module output [W] | 410
C14 - Nominal rated array output [W] | 1712.8934

## Tabelle2
1700 | 130
330
176
120
118
874
826
1066